## issues
遗留问题数据导入
责任部门 Dept | 责任人 Person in Charge | 责任QC QC in Charge | 当前状态 Status | 预计关闭日期 Estimated Close Date | PUNCH NUMBER | PUNCH DESCRIPTION | PUNCH STATE | ORIGINATOR | ORIGINATOR FULL NAME | ORIGINATOR COMPANY | ORIGIN DATE | PUNCH CATEGORY | PUNCH SOURCE | PUNCH SOURCE COMPLEMENT | ACTION BY | PUNCH DISCIPLINE | COMPANIES ALLOWED TO APPROVE AND CLOSE | ASSIGNEE | ASSIGNEE FULL NAME | ASSIGNEE COMPANY | TARGET DATE | RELATED PUNCHES | COMMENTS COUNT | VALIDATED BY | VALIDATION SIGNATORY FULL NAME | VALIDATION.SIGNATURE.SIGNATORY.COMPANY | VALIDATION DATE | VALIDATION | CARRIED OUT BY | CLEARANCE SIGNATORY FULL NAME | CLEARANCE.SIGNATURE.SIGNATORY.COMPANY | CARRIED OUT DATE | CARRIED OUT OUTCOME | VERIFIED BY | VERIFICATION SIGNATORY FULL NAME | VERIFICATION.SIGNATURE.SIGNATORY.COMPANY | VERIFICATION DATE | VERIFICATION OUTCOME | APPROVED BY | APPROVAL SIGNATORY FULL NAME | APPROVAL.SIGNATURE.SIGNATORY.COMPANY | APPROVAL DATE | APPROVAL | CANCELLED BY | CANCELLATION SIGNATORY FULL NAME | CANCELLATION.SIGNATURE.SIGNATORY.COMPANY | CANCELLATION DATE | CANCELLATION | DISPUTED | COMPANY IN CHARGE / CONTRACT | CONTRACT DESCRIPTION | COMPANY | WORK LOCATION | TAG | AREA/MODULE | SUBSYSTEM
内装 | 张大鹏 | 穆海峰 | 0 | 2021-06-12 | 21658 | RFI-HVA-35936-(D122550).All penetration to be properly sealed and insulated | Punch Created | jquiban | Jave Quiban | CONTRACTOR | 26-May-2021 | B | INSP | RFI-HVA-35936 | CONST | 21 |  |  |  |  | 15-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 1-BLM1-D122250-EA | T1R1B1 | 1-BLM-001-BL-95-01
内装 | 张大鹏 | 穆海峰 | 0 | 2021-06-12 | 21657 | RFI-HVA-35936-(D122550).Dampers to be properly insulated | Punch Created | jquiban | Jave Quiban | CONTRACTOR | 26-May-2021 | B | INSP | RFI-HVA-35936 | CONST | 21 |  |  |  |  | 15-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 1-BLM1-D122250-EA | T1R1B1 | 1-BLM-001-BL-95-01
内装 | 张大鹏 | 穆海峰 | 0 | 2021-06-12 | 21656 | RFI-HVA-35936-(D122550).All penetration to be properly sealed, insulated and fire stop sealant to be provided | Punch Created | jquiban | Jave Quiban | CONTRACTOR | 26-May-2021 | B | INSP | RFI-HVA-35936 | CONST | 21 |  |  |  |  | 15-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 1-BLM1-D122250-FA | T1R1B1 | 1-BLM-001-BL-95-01
内装 | 张大鹏 | 穆海峰 | 0 | 2021-06-12 | 21655 | RFI-HVA-35936-(D122550).Poor Application of Insulation and Damaged insulation to be rectified | Punch Created | jquiban | Jave Quiban | CONTRACTOR | 26-May-2021 | B | INSP | RFI-HVA-35936 | CONST | 21 |  |  |  |  | 15-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 1-BLM1-D122250-FA | T1R1B1 | 1-BLM-001-BL-95-01
加设 | 杨琼 | 穆海峰 | 0 | 2021-06-12 | 21654 | RFI-HVA-26411-(D122550).TP to be installed properly | Punch Created | jhu3 | Jianjun Hu | CONTRACTOR | 26-May-2021 | B | INSP | RFI-HVA-26411 | CONST | 21 |  |  |  |  | 15-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 1-BLM1-D122250-FA | T1R1B1 | 1-BLM-001-BL-95-01
内装 | 张大鹏 | 穆海峰 | 0 | 2021-06-12 | 21653 | RFI-HVA-26411-(D122550).Fire Rated Sealant to be applied in Fire Penetration to Sandwich Panel Connection and Insulation to be verified and certified by Insulation Inspector | Punch Created | jhu3 | Jianjun Hu | CONTRACTOR | 26-May-2021 | B | INSP | RFI-HVA-26411 | CONST | 21 |  |  |  |  | 15-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 1-BLM1-D122250-FA | T1R1B1 | 1-BLM-001-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-04 | 21649 | Damaged instrumnet cable tray on AHU(195-U-010B) to be replaced. | Punch Created | choi.bogbai | choi bogbai | NOVATEK | 29-May-2021 | B | WD |  | CONST | 15 |  |  |  |  | 05-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 195-PDIT-20181 | T1R1B1 | 1-BLM-001-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-04 | 21648 | No cable tag，location tag， hanging tag on instrument. | Punch Created | choi.bogbai | choi bogbai | NOVATEK | 29-May-2021 | B | WD |  | CONST | 15 |  |  |  |  | 05-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 195-FIT-00105 | T1R1B1 | 1-BLM-001-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-24 | 21437 | Cable ferrule size can't match with bolt at side.115-KM-900A-VSD/900K-VSD | Punch Created | yuezhiwei_Applus | Zhiwei Yue | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-E&I-40586 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-115-KM-900A-VSD-1 | T1R1B1 | 115-P-05
调试 | 王峥 | 0 | 0 | 0 | 21024 | Utility power is not ready, cabinet lamp tests not done. | Punch Created | yzhang19 | Yili Zhang | CONTRACTOR | 27-May-2021 | B | INSP |  | CONST | 98 |  |  |  |  | 10-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | SAT-HVAC-1-BLM-001-01 | T1R1B1 | 1-BLM-001-BL-95-01
调试 | 王峥 | 0 | 0 | 0 | 21023 | communication cable (PH-108-C-D-003) NOT installed | Punch Created | yzhang19 | Yili Zhang | CONTRACTOR | 27-May-2021 | B | INSP |  | CONST | 98 |  |  |  |  | 10-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | SAT-HVAC-1-BLM-001-01 | T1R1B1 | 1-BLM-001-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-04 | 21008 | The door have corrosion of Cabinet Rear | Punch Created | mduan | Mingming Duan | CONTRACTOR | 27-May-2021 | B | INSP |  | CONST | 15 |  |  |  |  | 10-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | MCR-101-001 | T1R1B1 | 1-BLM-001-IN-94
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20947 | Cable on 195-SB101-N1B panel side missing support. | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | B | INSP | F217-RFI-EI-40606 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB101-N1B-1 | T1R1B1 | 1-BLM-001-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20946 | MCT(003) crash with cable which effict cable sealing. | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | B | INSP | F217-RFI-EI-40606 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB101-N1B-1 | T1R1B1 | 1-BLM-001-BL-95-01
加设 | 0 | 0 | 0 | 0 | 20945 | path of cable does not macth with drawing P101N-195-SB101-N1B-1 | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | B | INSP | F217-RFI-EI-40606 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB101-N1A-1 | T1R1B1 | 1-BLM-001-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20944 | There have obviously damage on the cable. | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-EI-40606 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB101-N1A-1 | T1R1B1 | 1-BLM-001-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20943 | Missing support at MCT/002 side. | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | B | INSP | F217-RFI-EI-40760 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB108-N1B-1 | T1R1B1 | 1-BLM-008-BL-95-01
加设 | 0 | 0 | 0 | 0 | 20942 | path of cable does not macth with drawing . | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | B | INSP | F217-RFI-EI-40760 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB108-N1B-1 | T1R1B1 | 1-BLM-008-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20941 | Missing support at 195-SB108-N1 panel and MCT/014 side. | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | B | INSP | F217-RFI-EI-40760 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB108-N1A-1 | T1R1B1 | 1-BLM-008-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20940 | bolts torque test not compent at both side.P101N-195-SB101-N1B-1 | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-EI-40762 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB108-N1A-1 | T1R1B1 | 1-BLM-008-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20936 | cable core ferule not suitable at UPS side. P101F-195-SB108-N1-AUX5-2 | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | B | INSP | F217-RFI-EI-40762 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101F-195-SB108-N1-AUX5-1 | T1R1B1 | 1-BLM-008-BL-95-01
加设 | 0 | 0 | 0 | 0 | 20935 | terminal strip tag(L14) ，drawing show N14 at 195-SB108-N1 side. P101N-195-SB101-N1B-1 | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-EI-40762 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB108-N1A-1 | T1R1B1 | 1-BLM-008-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20934 | Cable gland not installed properly,steel amour not compress with gland body P101N-195-SB108-N1B-1 . | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-EI-40762 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB108-N1A-1 | T1R1B1 | 1-BLM-008-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20932 | blots torque test not complete at both side P101N-195-SB101-N1B-1 | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-EI-40608 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB101-N1A-1 | T1R1B1 | 1-BLM-001-BL-95-01
加设 | 0 | 0 | 0 | 0 | 20931 | schematic diagram show L11：BR，L12：BK，L13：GR，wires diagram show L11：BK，L12：BR，L13：GR at 195-SB101-N1 panel side.P101N-195-SB101-N1B-1 | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-EI-40608 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB101-N1A-1 | T1R1B1 | 1-BLM-001-BL-95-01
加设 | 0 | 0 | 0 | 0 | 20930 | terminal strip tag(L14) ,drawing show (N14) at 195-SB101-N1 panel side .P101N-195-SB101-N1A-1 | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-EI-40608 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB101-N1B-1 | T1R1B1 | 1-BLM-001-BL-95-01
电仪-TMR1 | 王爱民 | 赵伟东 | 未关闭 | 2021-06-18 | 20929 | gland not installed properly,steel amour not compress with gland body P101N-195-SB101-N1A-1 . | Punch Created | wangxianyuan_Applus | xianyuan wang | CONTRACTOR | 26-May-2021 | A | INSP | F217-RFI-EI-40608 | CONST | 16 |  |  |  |  | 09-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | P101N-195-SB101-N1B-1 | T1R1B1 | 1-BLM-001-BL-95-01
电气 | 倪意舟 | 韩波 | 未关闭 | 2021-06-10 | 20927 | TE not installed. | Punch Created | choi.bogbai | choi bogbai | NOVATEK | 27-May-2021 | A | WD | HVAC commissioning | CONST | 21 |  |  |  |  | 10-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 195-TIT-20183 | T1R1B1 | 1-BLM-001-BL-95-01
电气 | 倪意舟 | 韩波 | 未关闭 | 2021-06-10 | 20926 | No cable tag./ No location tag/ fastened the cable with tie | Punch Created | choi.bogbai | choi bogbai | NOVATEK | 27-May-2021 | B | WD | HVAC commissioning | CONST | 21 |  |  |  |  | 10-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 195-TIT-20183 | T1R1B1 | 1-BLM-001-BL-95-01
电气 | 倪意舟 | 韩波 | 未关闭 | 2021-06-10 | 20925 | No cable tag./ No location tag/ fastened the cable with tie. /Cable not fixed | Punch Created | choi.bogbai | choi bogbai | NOVATEK | 27-May-2021 | B | WD | HVAC commissioning | CONST | 21 |  |  |  |  | 10-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 195-TT-00141 | T1R1B1 | 1-BLM-001-BL-95-01
电气 | 倪意舟 | 韩波 | 未关闭 | 2021-06-10 | 20924 | No cable tag./No location tag. / Cable no fixed./ TE protector. | Punch Created | choi.bogbai | choi bogbai | NOVATEK | 27-May-2021 | B | WD | HVAC commissioning | CONST | 21 |  |  |  |  | 10-Jun-2021 |  | 0 | [26 empty] | MWP01 | MODULE - MWP01 | WISON | ZHOUSHAN | 195-TT-00140 | T1R1B1 | 1-BLM-001-BL-95-01
Formulas:
预计关闭日期 Estimated Close Date = IF(COUNTIF([2]INPUT!G:G,[PUNCH NUMBER])>0,VLOOKUP([PUNCH NUMBER],[2]INPUT!A:G,6,FALSE),"TBC")

## styles
errors

## SETTINGS
Settings
NAME | No | Description
SHEET NAME | issues | sheet name
HEADER ROW | 2 | header row number

## COLUMNS
Settings
Column Name | Column Index | isTableColumn | Description
department | 0 | Y
personInCharge | 1 | Y
qc | 2 | Y
internalPunchStatus | 3 | Y
planFinishDate | 4 | Y
no | 5 | Y | 实际的列号，B=2
description | 6 | Y
punchStatus | 7 | Y
originator | 8 | Y
originatorFullName | 9 | Y
originatorCompany | 10 | Y
originDate | 11 | Y
punchCategory | 12 | Y
punchSource | 13 | Y
punchSourceComplement | 14 | N | PUNCH SOURCE COMPLEMENT
actionBy | 15 | N | ACTION BY
discipline | 16 | Y | PUNCH DISCIPLINE
companyAllowedToApproveAndClose | 17 | N | COMPANIES ALLOWED TO APPROVE AND CLOSE
assignee | 18 | N | ASSIGNEE
assigneeFullName | 19 | N | ASSIGNEE FULL NAME
assigneeCompany | 20 | N | ASSIGNEE COMPANY
targetDate | 21 | N | TARGET DATE
relatedPunches | 22 | N | RELATED PUNCHES
commentCount | 23 | N | COMMENTS COUNT
validatedBy | 24 | N | VALIDATED BY
validationSignatoryFullName | 25 | N | VALIDATION SIGNATORY FULL NAME
validationSignatureSignatoryCompany | 26 | N | VALIDATION.SIGNATURE.SIGNATORY.COMPANY
validationDate | 27 | N | VALIDATION DATE
validation | 28 | N | VALIDATION
carriedOutBy | 29 | N | CARRIED OUT BY
clearanceSignatoryFullName | 30 | N | CLEARANCE SIGNATORY FULL NAME
clearanceSignatureSignatoryCompany | 31 | N | CLEARANCE.SIGNATURE.SIGNATORY.COMPANY
carriedOutDate | 32 | N | CARRIED OUT DATE
carriedOutOutcome | 33 | N | CARRIED OUT OUTCOME
verifiedBy | 34 | N | VERIFIED BY
verificationSignatoryFullName | 35 | N | VERIFICATION SIGNATORY FULL NAME
verficationSignatureSignatoryCompany | 36 | N | VERIFICATION.SIGNATURE.SIGNATORY.COMPANY
verficationDate | 37 | N | VERIFICATION DATE
verificationOutcome | 38 | N | VERIFICATION OUTCOME
approvedBy | 39 | N | APPROVED BY
approvalSignatoryFullName | 40 | N | APPROVAL SIGNATORY FULL NAME
ApprovalSignarureSignatoryCompany | 41 | N | APPROVAL.SIGNATURE.SIGNATORY.COMPANY
approvalDate | 42 | N | APPROVAL DATE
approval | 43 | N | APPROVAL
cancelledBy | 44 | N | CANCELLED BY
cancellationSignatoryFullName | 45 | N | CANCELLATION SIGNATORY FULL NAME
cancellationSignatureSignatoryCompany | 46 | N | CANCELLATION.SIGNATURE.SIGNATORY.COMPANY
cancellationDate | 47 | N | CANCELLATION DATE
cancellation | 48 | N | CANCELLATION
disputed | 49 | N | DISPUTED
companyInChargeContract | 50 | N | COMPANY IN CHARGE / CONTRACT
contractDescription | 51 | N | CONTRACT DESCRIPTION
company | 52 | N | COMPANY
workLocation | 53 | N | WORK LOCATION
entities | 54 | Y | TAG
module | 55 | Y | AREA/MODULE
subSystem | 56 | Y | SUBSYSTEM